## Plan1
In a two wires assembly, we must consider the resistance of the wires connection between the element sensor and the temperature indicator/controller.
Input |  | Results
resistance increment (dR/dT): | 0.385 | Wire material resistivity (ρ): | 0.0172 | 10⁻⁶ Ohms.m @ 20°C
Wire material: | Copper | Wire cross section area (A): | 0.2043 | mm²
Wire diameter (D): | 24 AWG / Ø 0.51 mm | Resistance per meter of wire (R): | 0.08419 | Ohms
Wire length in millimeters (L): | 10000 | Measurement error per meter 2 wires (E): | 0.089351 | °C/m @ 20 °C
|  | Total measuring error of sensor: | 0.89351 | °C
This application was developed by Sensor Technology Ltda. All right reserved.
Technical responsible: Eng° Orlando Rodrigues dos Santos Filho
| www.sensor-technology.com.br | orlando.santos@sensor-technology.com.br
Resistance of a wire can be expressed as:
This resistance can vary in function of the characteristics of the wire, such as:
- wire diameter (A), alloying of metals, wire extension length, environment temperature and/or the media where the wire is installed.
To identify the error caused by the resistance of the conductors, we can use the formula below:
E°C/m = Error in °C per meter, proportional to the variables of the conductors Rc1 e Rc2.
Rc1 e Rc2 = Electrical resistance in ohm/m of the conductor. Both conductors must have the same characteristics
dR/dT = derivative dR/dT which represents the resistance increment in ohm/ºC. Also can be 0.3850, 0.3851, 0.3916 or 0.3923.
E°C/m = Rc1 + Rc2
dR/dT

## Plan2 (hidden)
0.3851
0.385
0.3916
0.3923
Aluminum | 0.0282
Copper | 0.0172
Silver | 0.0159
14 AWG / Ø 1.6 mm | 2.0106
15 AWG / Ø 1,5 mm | 1.7671
16 AWG / Ø 1.3 mm | 1.3273
17 AWG / Ø 1.2 mm | 1.131
18 AWG / Ø 1.0 mm | 0.7854
19 AWG / Ø 0.91 mm | 0.6504
20 AWG / Ø 0.81 mm | 0.5153
21 AWG / Ø 0.72 mm | 0.4072
22 AWG / Ø 0.64 mm | 0.3217
23 AWG / Ø 0.57 mm | 0.2552
24 AWG / Ø 0.51 mm | 0.2043
25 AWG / Ø 0.46 mm | 0.1662
26 AWG / Ø 0.41 mm | 0.132
27 AWG / Ø 0.36 mm | 0.1018
28 AWG / Ø 0.32 mm | 0.0804
29 AWG / Ø 0.29 mm | 0.0611
30 AWG / Ø 0.26 mm | 0.0531
31 AWG / Ø 0.23 mm | 0.0415
32 AWG / Ø 0.20 mm | 0.0314